## Alarm Rev - Critical 2 Pump
Alarm Review Workshop Results - TOMTEM01 |  |  | For guidelines on using this template refer to: TOMSTD02 - Alarm Philosophy for SCADA Alarms
Alarm Review Date: |  | HPRM Document Number: |  |  |  | TDETEM10 - v3.0 |  | Project Number/Job Reference: |  |  | Generic - Statewide Standard 2 Pump SPS Alarm Review - High Criticality Site |  |  |  | Document References: | TOMSTD02 -TasWater Alarm Philosophy for SCADA ALARMS TDESTD25 - Small Sewer Pump Station - Functional Description TDEMAN01 - Small Sewage Pump Station - O & M Manual TASPRO19 - Risk Management Procedure - Part B: Assessment Tools [Tool B: Strategic and Operational Consequence Assessment] TOMMAN21 State-Wide SCADA Head End – User Manual - Integrators TDESTD79 TasWater Standard Motor Circuit Functional Description and Alarm List TDESTD77 TasWater Standard Emergency Stop Circuit Functional Description Revision 1.0 TDESTD78 TasWater Standard 24VDC Power Supply Circuits Functional Description Revision 1.0 TDESTD103 TasWater Standard Motor Duty Control Functional Description
Facilitator
Attendees |  |  |  | Apologies
Site Criticality Assessment
Asset ID | As per the TasWater standard Asset ID from GIS | [7 empty] | Site Power / Backup Power |  |  | - The site is supplied from a dedicated 3 phase TasNetworks feed. - It is possible to connect a portable generator set to the SPS Switchboard if necesary. - The RTU/Radio/4G Router is supplied from a separate 24V power supply, with 4 hours battery backup
Asset Name | As per the TasWater description from GIS | [7 empty] | Critical Control Links to remote sites |  |  | None
Site Description | A SPS collects untreated sewage from residential, commercial and industrial customers. It pumps the sewerage to a sewerage treatment plant. There may be a number of SPS's in a network that pump from one to another. This needs to be considered for a site specific alarm review. | [7 empty] | Communications to HeadEnd/WAN for paging |  |  | Radio or 4G
Operation Philosophy | Automatic operation, refer to TDESTD25 Functional Description & TDEMAN01 - Small Sewage Pump Station - O & M Manual | [7 empty] | PLC/RTU/SCADA/ Alarm Type & System |  |  | Displayed on the Statewide Headend ClearSCADA system. Critical & High alarms monitored by NOC 24/7. Low Severity alarms by operations during business hours.
Typical Travel Time to Site - After Work Hours (ADD DETAILS TO SITE NOTES WITHIN SCADA) | Up to x Minutes | [7 empty] | Product Quality Requirements |  |  | None
Storage Capacity | Minimum of x Hours retention at average dry weather flow (ADWF). | [7 empty] | Leak Detection |  |  | None
Critical Customers | [8 empty] | Loss of Containment |  |  | High criticality spill, refer to risk assessment
[9 empty] | Redundant Process Equipment |  |  | Duty Standby OR Duty Assist
Point Name Prefix | As per SCADA Point Naming Convention - Sewer.X.Y. | [7 empty] | Other
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Equipment.Pump 1.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump 1.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump 1.Not in Auto | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 1.Isolated | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 1.Fault | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Failed to Start | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | Attempt to reset from SCADA once, if it fails, Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump 1.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump 1.Flow Low | Alarm | Environment | Major | Immediate | Critical | None | NA | Adjustable | 0 - 100 % | SCADA Engineer | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Oil Seal Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | 1 Second | Pump Not in Auto | Oil Seal, Bearing, etc failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump 2.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump 2.Not in Auto | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 1.Isolated | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 2.Fault | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Failed to Start | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | Attempt to reset from SCADA once, if it fails, Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump 2.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump 2.Flow Low | Alarm | Environment | Major | Immediate | Critical | None | NA | Adjustable | 0 - 100 % | SCADA Engineer | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Oil Seal Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | 1 Second | Pump Not in Auto | Oil Seal, Bearing, etc failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Emergency Stop | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | Field Reset | None | None |  | Call local operator and create Work Order | Attend site and inspect | After e-stop is activated and then released, both pump reset buttons are required to to pushed before they can restart.
Equipment.Station.Intrusion Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Keyswitch | Refer FD | None | Key Switch not Activated | Check site activity, if necessary call local operator and create Work Order | Attend site and inspect
Equipment.Station.No Pumps Available | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | None | None | Pump(s) not in Auto, Isolated or Faulted | Check SCADA to confirm reason for unavailability. Call local operator or electrician, and create Work Order | Attend site and inspect
Equipment.Station.Pump Starts Overdue | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0 - 240 Hours | Operator | 24 Hours | Not Latched | Auto Reset | Refer FD | Main Supply - Off. Estop, atleast 1 pump available, Alarm inhibited if Setpoint = 0 | Likely an issue in the reticulation system | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Low Alarm | Alarm | Environment | Moderate | 24 Hours | High | None | NA | Site Specific | Between 0 and Low Float Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level Transmitter Alarm, low float didn't activate when expected. Could happen if a float test fails, or if a high float activates the pumps and the low float fails to stop the pumps. Check float. | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Level TX Fault Low Float out of Position Float failed | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Level TX Loop Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | Level TX Fault or wiring fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Overflow | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between Emerg Inflow Position and Top of Well | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm. High High alarm should have been activated and responded to | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High High Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between High Float Position and Emerg Inflow Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm | Call local operator and create Work Order. For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. | For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. Attend site and inspect, request pump truck.
Equipment.Wet Well.High Float Sustained | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | Float Tipped for 2 Minutes | None | Float Tipped for 2 Minutes | Call local operator and create Work Order. For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. | For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. Attend site and inspect, request pump truck.
Equipment.Wet Well.High Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Discrepency between high float and level TX | Call local operator and create Work Order | Attend site and inspect
Equipment.Power.Mains Surge Device | Alarm | Property | 2 | 24 Hours | High | None | N/A | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Lightning strike | Create Work Order and call Electrician | Attend site, Replace surge diverter.
Equipment.Power.Main Supply Failed | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | 0-7200 min | SCADA Engineer | NA | Site Specific | Auto Reset | 10 Minute Delay (Confirm in alarm review) | None | TasNetworks or Generator Power supply failed. Detected by a phase failure relay. | Contact TasNetworks. Review wet well level. This is a high criticality site. If level change is low a call out may not be required. | Attend site and inspect if required
Equipment.Power.DC Supply 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.DC Supply 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Both DC Supplies Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | 24VDC Charger Fault or Loss of AC Supply to DC Charger (across both chargers/supplies) | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual supply faults that are then summarised by this alarm
Equipment.Power.Both Batteries Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Both batteries running low | This is a high criticality site. Create work order and monitor site to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual battery faults that are then summarised by this alarm
Equipment.Power.DC Protection Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | One or more 24VDC distribution breakers tripped | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A
Equipment.RTU.Hardware Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Issue with 1 or more RTU modules or backplane | Create Work Order and call Electrician | N/A
Equipment.Station.Odour Fan CB | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Overload tripped. | N/A | Attend site and inspect
Equipment.Station.Odour Fan Not in Auto | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Man-Off-Auto switch not in the Auto position | N/A | Attend site and inspect
Equipment.Flow.Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Flow.Device Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Wet Well.Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Wet Well.E Storage Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Station.Smoke Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | NA | None | Yes | Call Tasfire, then call local operator and create Work Order | Check site activity | Do not enter building without Tas Fire present
Equipment.RTU.Outstation.Communications State - Failed | Alarm | Reputation | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 30 Minute Delay (Confirm in alarm review) | None | Radio or 3G Fault depending on site | Radio: Check radio comms status with SCADA group 4G: Check Telstra Outages via TasWater business systems | N/A | Delay built in at SCADA, Attend site and pump down the well, if required. Check the modem is powered (indicator lights)

## Alarm Rev - Non Critical 2 Pump
Alarm Review Workshop Results - TOMTEM01 |  |  | For guidelines on using this template refer to: TOMSTD02 - Alarm Philosophy for SCADA Alarms
Alarm Review Date: |  | HPRM Document Number: |  |  |  | TDETEM10 - v3.0 |  | Project Number/Job Reference: |  |  | Generic - Statewide Standard 2 Pump SPS Alarm Review - Low Criticality Site |  |  |  | Document References: | TOMSTD02 -TasWater Alarm Philosophy for SCADA ALARMS TDESTD25 - Small Sewer Pump Station - Functional Description TDEMAN01 - Small Sewage Pump Station - O & M Manual TASPRO19 - Risk Management Procedure - Part B: Assessment Tools [Tool B: Strategic and Operational Consequence Assessment] TOMMAN21 State-Wide SCADA Head End – User Manual - Integrators TDESTD79 TasWater Standard Motor Circuit Functional Description and Alarm List TDESTD77 TasWater Standard Emergency Stop Circuit Functional Description Revision 1.0 TDESTD78 TasWater Standard 24VDC Power Supply Circuits Functional Description Revision 1.0 TDESTD103 TasWater Standard Motor Duty Control Functional Description
Facilitator
Attendees |  |  |  | Apologies
Site Criticality Assessment
Asset ID | As per the TasWater standard Asset ID from GIS | [7 empty] | Site Power / Backup Power |  |  | - The site is supplied from a dedicated 3 phase TasNetwors feed. - It is possible to connect a portable generator set to the SPS Switchboard if necesary. - The RTU/Radio/3G Router is supplied from a separate 24V power supply, with 4 hours battery backup
Asset Name | As per the TasWater description from GIS | [7 empty] | Critical Control Links to remote sites |  |  | None
Site Description | A SPS collects untreated sewage from residential, commercial and industrial customers. It pumps the sewerage to a sewerage treatment plant. There may be a number of SPS's in a network that pump from one to another. This needs to be considered for a site specific alarm review. | [7 empty] | Communications to HeadEnd/WAN for paging |  |  | Radio or 3G
Operation Philosophy | Automatic operation, refer to TDESTD25 Functional Description & TDEMAN01 - Small Sewage Pump Station - O & M Manual | [7 empty] | PLC/RTU/SCADA/ Alarm Type & System |  |  | Displayed on the Statewide Headend ClearSCADA system. Critical & High alarms monitored by NOC 24/7. Low Severity alarms by operations during business hours.
Typical Travel Time to Site - After Work Hours | Up to x Minutes | [7 empty] | Product Quality Requirements |  |  | None
Storage Capacity | Minimum of x Hours retention at average dry weather flow (ADWF). | [7 empty] | Leak Detection |  |  | None
Critical Customers | None | [7 empty] | Loss of Containment |  |  | Low criticality spill, refer to risk assessment
[9 empty] | Redundant Process Equipment |  |  | Duty Standby OR Duty Assist
Point Name Prefix | As per SCADA Point Naming Convention - Sewer.X.Y. | [7 empty] | Other
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Equipment.Pump 1.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump 1.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump 1.Not in Auto | Alarm | Service | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 1.Isolated | Alarm | Service | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 1.Fault | Alarm | Service | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | N/A | Work Order and attend site
Equipment.Pump 1.Failed to Start | Alarm | Service | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | N/A | Work Order and attend site
Equipment.Pump 1.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump 1.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump 1.Flow Low | Alarm | Property | Minor | 24 Hours | High | None | NA | Adjustable | 0 - 50 | Operator | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 1.Oil Seal Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | 10 Seconds | Pump Not in Auto | Seal Failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump 2.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump 2.Not in Auto | Alarm | Service | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 2.Isolated | Alarm | Service | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump 2.Fault | Alarm | Service | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | N/A | Work Order and attend site
Equipment.Pump 2.Failed to Start | Alarm | Service | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | N/A | Work Order and attend site
Equipment.Pump 2.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump 2.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump 2.Flow Low | Alarm | Property | Minor | 24 Hours | High | None | NA | Adjustable | 0 - 50 | Operator | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump 2.Oil Seal Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | Pump Not in Auto | Seal Failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Emergency Stop | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | None |  | Call local operator and create Work Order | Attend site and inspect | After e-stop is activated and then released, both pump reset buttons are required to to pushed before they can restart.
Equipment.Station.Intrusion Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Keyswitch | Refer FD | None | Key Switch not Activated | Check site activity, if necessary call local operator and create Work Order | Attend site and inspect
Equipment.Station.No Pumps Available | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | None | None | Pump(s) not in Auto, Isolated or Faulted | Check SCADA to confirm reason for unavailability. Call local operator or electrician, and create Work Order | Attend site and inspect
Equipment.Station.Pump Starts Overdue | Alarm | Environment | Moderate | 24 Hours | High | None | NA | Adjustable | 0 - 240 Hours | Operator | 24 Hours | Not Latched | Auto Reset | Refer FD | Main Supply - Off. Estop, atleast 1 pump available, Alarm inhibited if Setpoint = 0 | Likely an issue in the reticulation system | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Low Alarm | Alarm | Environment | Moderate | 24 Hours | High | None | NA | Site Specific | Between 0 and Low Float Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level Transmitter Alarm, low float didn't activate when expected. Could happen if a float test fails, or if a high float activates the pumps and the low float fails to stop the pumps. Check float. | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Level TX Fault Low Float out of Position Float failed | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Level TX Loop Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | Level TX Fault or wiring fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Overflow | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between Emerg Inflow Position and Top of Well | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm. High High alarm should have been activated and responded to. | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High High Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between High Float Position and Emerg Inflow Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm. | Call local operator and create Work Order. For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. | For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. Attend site and inspect, request pump truck.
Equipment.Wet Well.High Float Sustained | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | Float Tipped for 2 Minutes | None | Float Tipped for 2 Minutes | Call local operator and create Work Order. For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. | For Duty/Standby Sites ONLY - Consider changing pump duty to see if the second pump can handle the inflow. Attend site and inspect, request pump truck.
Equipment.Wet Well.High Float Position Fault | Alarm | Property | Minor | 1 Week | Low | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Discrepency between high float and level TX | N/A | Work Order and attend site
Equipment.Power.Mains Surge Device | Alarm | Property | 2 | 24 Hours | High | None | N/A | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Lightning strike | Create Work Order and call Electrician | Attend site, Replace surge diverter.
Equipment.Power.Main Supply Failed | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | 0-7200 min | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 30 Minute Delay | None | TasNetworks or Generator Power supply failed. Detected by a phase failure relay. | Contact TasNetworks. Review wet well level. This is a high criticality site. If level change is low a call out may not be required. | Attend site and inspect if required
Equipment.Power.DC Supply 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.DC Supply 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Both DC Supplies Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | 24VDC Charger Fault or Loss of AC Supply to DC Charger (across both chargers/supplies) | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual supply faults that are then summarised by this alarm
Equipment.Power.Both Batteries Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Both batteries running low | This is a high criticality site. Create work order and monitor site to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual battery faults that are then summarised by this alarm
Equipment.Power.DC Protection Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | One or more 24VDC distribution breakers tripped | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A
Equipment.RTU.Hardware Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Issue with 1 or more RTU modules or backplane | Create Work Order and call Electrician | N/A
Equipment.RTU.Internal Battery Voltage Low | Alarm | Property | Minor | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | RTU Internal Battery Failure | Create Work Order and call Electrician | N/A
Equipment.Station.Odour Fan CB | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Overload tripped. | N/A | Attend site and inspect
Equipment.Station.Odour Fan Not in Auto | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Man-Off-Auto switch not in the Auto position | N/A | Attend site and inspect
Equipment.Flow.Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Flow.Device Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Wet Well.Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Wet Well.E Storage Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Station.Smoke Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | NA | None | Yes | Call Tasfire, then call local operator and create Work Order | Check site activity | Do not enter building without Tas Fire present
Equipment.RTU.Outstation.Communications State - Failed | Alarm | Reputation | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 30 Minute Delay | None | Radio or 3G Fault depending on site | Radio: Check radio comms status with SCADA group 3/4G: Check Telstra Outages via TasWater business systems | N/A | Delay built in at SCADA, Attend site and pump down the well, if required. Check the modem is powered (indicator lights)

## Alarm Rev - Critical 1 Pump
Alarm Review Workshop Results - TOMTEM01 |  |  | For guidelines on using this template refer to: TOMSTD02 - Alarm Philosophy for SCADA Alarms
Alarm Review Date: |  | HPRM Document Number: |  |  |  | TDETEM10 - v3.0 |  | Project Number/Job Reference: |  |  | Generic - Statewide Standard 2 Pump SPS with 1 Pump ONLY Alarm Review - High Criticality Site |  |  |  | Document References: | TOMSTD02 -TasWater Alarm Philosophy for SCADA ALARMS TDESTD25 - Small Sewer Pump Station - Functional Description TDEMAN01 - Small Sewage Pump Station - O & M Manual TASPRO19 - Risk Management Procedure - Part B: Assessment Tools [Tool B: Strategic and Operational Consequence Assessment] TOMMAN21 State-Wide SCADA Head End – User Manual - Integrators TDESTD79 TasWater Standard Motor Circuit Functional Description and Alarm List TDESTD77 TasWater Standard Emergency Stop Circuit Functional Description Revision 1.0 TDESTD78 TasWater Standard 24VDC Power Supply Circuits Functional Description Revision 1.0 TDESTD103 TasWater Standard Motor Duty Control Functional Description
Facilitator
Attendees |  |  |  | Apologies
Site Criticality Assessment
Asset ID | As per the TasWater standard Asset ID from GIS | [7 empty] | Site Power / Backup Power |  |  | - The site is supplied from a dedicated 3 phase TasNetworks feed. - It is possible to connect a portable generator set to the SPS Switchboard if necesary. - The RTU/Radio/3G Router is supplied from a separate 24V power supply, with 4 hours battery backup
Asset Name | As per the TasWater description from GIS | [7 empty] | Critical Control Links to remote sites |  |  | None
Site Description | A SPS collects untreated sewage from residential, commercial and industrial customers. It pumps the sewerage to a sewerage treatment plant. There may be a number of SPS's in a network that pump from one to another. This needs to be considered for a site specific alarm review. | [7 empty] | Communications to HeadEnd/WAN for paging |  |  | Radio or 3G
Operation Philosophy | Automatic operation, refer to TDESTD25 Functional Description & TDEMAN01 - Small Sewage Pump Station - O & M Manual | [7 empty] | PLC/RTU/SCADA/ Alarm Type & System |  |  | Displayed on the Statewide Headend ClearSCADA system. Critical & High alarms monitored by NOC 24/7. Low Severity alarms by operations during business hours.
Typical Travel Time to Site - After Work Hours | Up to x Minutes | [7 empty] | Product Quality Requirements |  |  | None
Storage Capacity | Minimum of x Hours retention at average dry weather flow (ADWF). | [7 empty] | Leak Detection |  |  | None
Critical Customers | None | [7 empty] | Loss of Containment |  |  | High criticality spill, refer to risk assessment
[9 empty] | Redundant Process Equipment |  |  | Duty Only
Point Name Prefix | As per SCADA Point Naming Convention - Sewer.X.Y. | [7 empty] | Other
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Equipment.Pump.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump.Not in Auto | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump.Isolated | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump.Fault | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | Call local operator and create Work Order | Attend site and inspect, attenpt to reset
Equipment.Pump.Failed to Start | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | Attempt to reset from SCADA once, if it fails, Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump.Flow Low | Alarm | Property | Major | Immediate | Critical | None | NA | Adjustable | 0 - 100 % | SCADA Engineer | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Oil Seal Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | Pump Not in Auto | Oil Seal, Bearing, etc failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Emergency Stop | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | None |  | Call local operator and create Work Order | Attend site and inspect | After e-stop is activated and then released, both pump reset buttons are required to to pushed before they can restart.
Equipment.Station.Intrusion Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Keyswitch | Refer FD | None | Key Switch not Activated | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Pump Starts Overdue | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0 - 240 Hours | Operator | 24 Hours | Not Latched | Auto Reset | Refer FD | Main Supply - Off. Estop, atleast 1 pump available, Alarm inhibited if Setpoint = 0 | Likely an issue in the reticulation system | Assess trends, Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Low Alarm | Alarm | Environment | Moderate | 24 Hours | High | None | NA | Site Specific | Between 0 and Low Float Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level Transmitter Alarm, low float didn't activate when expected. Could happen if a float test fails, or if a high float activates the pumps and the low float fails to stop the pumps. Check float. | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Level TX Fault Low Float out of Position Float failed | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Level TX Loop Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | Level TX Fault or wiring fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Overflow | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between Emerg Inflow Position and Top of Well | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm. High High alarm should have been activated and responded to | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High High Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between High Float Position and Emerg Inflow Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High Float Sustained | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | Float Tipped for 2 Minutes | None | Float Tipped for 2 Minutes | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Discrepency between high float and level TX | Call local operator and create Work Order | Attend site and inspect
Equipment.Power.Mains Surge Device | Alarm | Property | 2 | 24 Hours | High | None | N/A | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Lightning strike | Create Work Order and call Electrician | Attend site, Replace surge diverter.
Equipment.Power.Main Supply Failed | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | 0-7200 min | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 10 Minute Delay | None | TasNetworks or Generator Power supply failed. Detected by a phase failure relay. | Contact TasNetworks. Review wet well level. This is a high criticality site. If level change is low a call out may not be required. | Attend site and inspect if required
Equipment.Power.DC Supply 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.DC Supply 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 1 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Battery 2 Fault | Alarm | Environment | Moderate | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.Both DC Supplies Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | 24VDC Charger Fault or Loss of AC Supply to DC Charger (across both chargers/supplies) | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual supply faults that are then summarised by this alarm
Equipment.Power.Both Batteries Faulted | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Both batteries running low | This is a high criticality site. Create work order and monitor site to determine if someone (electrician) must attend site immediately or wait until business hours | N/A | Suppression handled by individual battery faults that are then summarised by this alarm
Equipment.Power.DC Protection Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | One or more 24VDC distribution breakers tripped | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A
Equipment.RTU.Hardware Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Issue with 1 or more RTU modules or backplane | Create Work Order and call Electrician | N/A
Equipment.RTU.Internal Battery Voltage Low | Alarm | Property | Minor | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | RTU Internal Battery Failure | Create Work Order and call Electrician | N/A
Equipment.Station.Odour Fan CB | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Overload tripped. | N/A | Attend site and inspect
Equipment.Station.Odour Fan Not in Auto | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Man-Off-Auto switch not in the Auto position | N/A | Attend site and inspect
Equipment.Flow.Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | RTU DC Voltage Low | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Flow.Device Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Wet Well.Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Wet Well.E Storage Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Station.Smoke Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | NA | None | Yes | Call Tasfire, then call local operator and create Work Order | Check site activity | Do not enter building without Tas Fire present
Equipment.RTU.Outstation.Communications State - Failed | Alarm | Reputation | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 30 Minute Delay | None | Radio or 3G Fault depending on site | Radio: Check radio comms status with SCADA group 3/4G: Check Telstra Outages via TasWater business systems | N/A | Delay built in at SCADA, Attend site and pump down the well, if required. Check the modem is powered (indicator lights)

## Alarm Rev - Non Critical 1 Pump
Alarm Review Workshop Results - TOMTEM01 |  |  | For guidelines on using this template refer to: TOMSTD02 - Alarm Philosophy for SCADA Alarms
Alarm Review Date: |  | HPRM Document Number: |  |  |  | TDETEM10 - v3.0 |  | Project Number/Job Reference: |  |  | Generic - Statewide Standard 1 Pump SPS with 1 Pump ONLY switchboard Alarm Review - Low Criticality Site |  |  |  | Document References: | TOMSTD02 -TasWater Alarm Philosophy for SCADA ALARMS TDESTD25 - Small Sewer Pump Station - Functional Description TDEMAN01 - Small Sewage Pump Station - O & M Manual TASPRO19 - Risk Management Procedure - Part B: Assessment Tools [Tool B: Strategic and Operational Consequence Assessment] TOMMAN21 State-Wide SCADA Head End – User Manual - Integrators TDESTD79 TasWater Standard Motor Circuit Functional Description and Alarm List TDESTD77 TasWater Standard Emergency Stop Circuit Functional Description Revision 1.0 TDESTD78 TasWater Standard 24VDC Power Supply Circuits Functional Description Revision 1.0 TDESTD103 TasWater Standard Motor Duty Control Functional Description
Facilitator
Attendees |  |  |  | Apologies
Site Criticality Assessment
Asset ID | As per the TasWater standard Asset ID from GIS | [7 empty] | Site Power / Backup Power |  |  | - The site is supplied from a dedicated 3 phase TasNetworks feed. - The RTU/Radio/3G Router is supplied from a separate 24V power supply, with 4 hours battery backup
Asset Name | As per the TasWater description from GIS | [7 empty] | Critical Control Links to remote sites |  |  | None
Site Description | A SPS collects untreated sewage from residential, commercial and industrial customers. It pumps the sewerage to a sewerage treatment plant. There may be a number of SPS's in a network that pump from one to another. This needs to be considered for a site specific alarm review. | [7 empty] | Communications to HeadEnd/WAN for paging |  |  | Radio or 3G
Operation Philosophy | Automatic operation, refer to TDESTD25 Functional Description & TDEMAN01 - Small Sewage Pump Station - O & M Manual | [7 empty] | PLC/RTU/SCADA/ Alarm Type & System |  |  | Displayed on the Statewide Headend ClearSCADA system. Critical & High alarms monitored by NOC 24/7. Low Severity alarms by operations during business hours.
Typical Travel Time to Site - After Work Hours | Up to x Minutes | [7 empty] | Product Quality Requirements |  |  | None
Storage Capacity | Minimum of x Hours retention at average dry weather flow (ADWF). | [7 empty] | Leak Detection |  |  | None
Critical Customers | None | [7 empty] | Loss of Containment |  |  | Low criticality spill, refer to risk assessment
[9 empty] | Redundant Process Equipment |  |  | Duty Only
Point Name Prefix | As per SCADA Point Naming Convention - Sewer.X.Y. | [7 empty] | Other
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Point Name | Alarm Assignment | Consequence Type | Consequence Rating | Time To Rectify | Alarm Severity | Escalation | Escalation Delay | Alarm Setpoint | Setpoint Range (Min-Max) | Setpoint Change Authority | Default Setpoint | Latched Alarm? | Alarm Reset | Filtering/Delays | Suppression | Possible Causes | OCC Corrective Actions | Local Corrective Actions | Notes
Equipment.Pump.Current High Alarm | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Adjustable | 0-50A | Operator | > 110% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pipe break, ragging of pump, incorrect setpoint, non-return valve failure | N/A | Work Order and attend site
Equipment.Pump.Current Low Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0-50A | SCADA Engineer | < 70% FLC | Latched | SCADA Device Reset | 30 Seconds | Loop Fault, Pump Not Running | Pump issues, blockages, low level | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Current Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA Device Reset | 10 Seconds | Main Supply - Off, Pump Isolated | CT/Soft Starter/Wiring Issue | N/A | Work Order and attend site
Equipment.Pump.Not in Auto | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump OFF or MANUAL at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump.Isolated | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 1 Second | None | Operator has left pump isolated at site | Call local operator and create Work Order | Attend site and inspect | Should only be an issue if the switch is inadvertently left in the position for an extended period.
Equipment.Pump.Fault | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Field Reset | 1 Second | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Overload trip or motor thermistor fault | Call local operator and create Work Order | Attend site and inspect, attenpt to reset
Equipment.Pump.Failed to Start | Alarm | Service | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | SCADA Device Reset | 10 Seconds | E-Stop, Main Supply - Off Pump Not in Auto, Pump Isolated | Motor contactor issue, relay or wiring issue | Attempt to reset from SCADA once, if it fails, Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Failed to Stop | Alarm | Financial | Insignificant | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 10 Seconds | Pump Not in Auto | Motor contactor issue, relay or wiring issue | Create Work Order and call Electrician | N/A
Equipment.Pump.Starts Excessive | Alarm | Property | Minor | 1 Week | Low | None | NA | Adjustable | 0 - 100 | Operator | 10 | Not Latched | Auto Reset | None | None | Float issues, infiltration | N/A | Work Order and attend site | Will automatically reset once the number of starts in the last hour drops below the excesive starts setpoint.
Equipment.Pump.Flow Low | Alarm | Property | Major | Immediate | Critical | None | NA | Adjustable | 0 - 100 % | SCADA Engineer | ~50% of Normal Flow | Latched | SCADA Device Reset | 60 Seconds | Flow Loop Fault, Flow Device Fault, Pump Not Running | Blockage, Ragging of pump, non-return valve failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Pump.Oil Seal Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | Pump Not in Auto | Oil Seal, Bearing, etc failure | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Emergency Stop | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Latched | Field Reset | NA | None |  | Call local operator and create Work Order | Attend site and inspect | After e-stop is activated and then released, both pump reset buttons are required to to pushed before they can restart.
Equipment.Station.Intrusion Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Keyswitch | Refer FD | None | Key Switch not Activated | Call local operator and create Work Order | Attend site and inspect
Equipment.Station.Pump Starts Overdue | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Adjustable | 0 - 240 Hours | Operator | 24 Hours | Not Latched | Auto Reset | Refer FD | Main Supply - Off. Estop, atleast 1 pump available, Alarm inhibited if Setpoint = 0 | Likely an issue in the reticulation system | Assess trends, Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Low Alarm | Alarm | Environment | Moderate | 24 Hours | High | None | NA | Site Specific | Between 0 and Low Float Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level Transmitter Alarm, low float didn't activate when expected. Could happen if a float test fails, or if a high float activates the pumps and the low float fails to stop the pumps. Check float. | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Low Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Level TX Fault Low Float out of Position Float failed | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Level TX Loop Fault | Alarm | Property | Insignificant | 24 Hours | High | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | Level TX Fault or wiring fault | Call local operator and create Work Order | Attend site and inspect
Equipment.Wet Well.Overflow | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between Emerg Inflow Position and Top of Well | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm. High High alarm should have been activated and responded to | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High High Alarm | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | Between High Float Position and Emerg Inflow Position | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 1 Second, Hysteresis built in to level ±50mm | Loop Fault | Level TX Alarm | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High Float Sustained | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | Float Tipped for 2 Minutes | None | Float Tipped for 2 Minutes | Call local operator and create Work Order | Attend site and inspect, request pump truck
Equipment.Wet Well.High Float Position Fault | Alarm | Property | Minor | 24 Hours | High | None | NA | Site Specific | Refer FD | SCADA Engineer | Site Specific | Latched | SCADA General Reset | Refer FD | Loop Fault | Discrepency between high float and level TX | Call local operator and create Work Order | Attend site and inspect
Equipment.Power.Mains Surge Device | Alarm | Property | 2 | 24 Hours | High | None | N/A | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Lightning strike | Create Work Order and call Electrician | Attend site, Replace surge diverter.
Equipment.Power.Main Supply Failed | Alarm | Environment | Moderate | Immediate | Critical | None | NA | Site Specific | 0-7200 min | SCADA Engineer | Site Specific | Not Latched | Auto Reset | 10 Minute Delay | None | TasNetworks or Generator Power supply failed. Detected by a phase failure relay. | Contact TasNetworks. Review wet well level. This is a high criticality site. If level change is low a call out may not be required. | Attend site and inspect if required
Equipment.Power.DC Supply Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | Main Supply - Off | 24VDC Charger Fault or Loss of AC Supply to DC Charger | N/A | Create Work Order and call Electrician
Equipment.Power.Battery Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Battery running low | N/A | Create Work Order and call Electrician
Equipment.Power.DC Protection Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | One or more 24VDC distribution breakers tripped | This is a high criticality site. Create work order and monitor wet well level to determine if someone (electrician) must attend site immediately or wait until business hours | N/A
Equipment.RTU.Hardware Fault | Alarm | Environment | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Issue with 1 or more RTU modules or backplane | Create Work Order and call Electrician | N/A
Equipment.RTU.Internal Battery Voltage Low | Alarm | Property | Minor | Immediate | High | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | RTU Internal Battery Failure | Create Work Order and call Electrician | N/A
Equipment.Station.Odour Fan CB | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Overload tripped. | N/A | Attend site and inspect
Equipment.Station.Odour Fan Not in Auto | Alarm | Reputation | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None | Man-Off-Auto switch not in the Auto position | N/A | Attend site and inspect
Equipment.Flow.Loop Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | RTU DC Voltage Low | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Flow.Device Fault | Alarm | Property | Insignificant | 1 Week | Low | None | NA | Refer FD | NA | NA | Refer FD | Latched | SCADA General Reset | 2 Seconds | None | TX Fault or wiring fault | N/A | Create Work Order and call Electrician
Equipment.Wet Well.Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Wet Well.E Storage Washer Not in Auto | Alarm | Property | Insignificant | 1 Week | Low | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | No Delay | None |  | N/A | Attend site and inspect
Equipment.Station.Smoke Alarm | Alarm | HSE | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | NA | None | Yes | Call Tasfire, then call local operator and create Work Order | Check site activity | Do not enter building without Tas Fire present
Equipment.RTU.Outstation.Communications State - Failed | Alarm | Reputation | Moderate | Immediate | Critical | None | NA | NA | NA | NA | NA | Not Latched | Auto Reset | 30 Minute Delay | None | Radio or 3G Fault depending on site | Radio: Check radio comms status with SCADA group 3/4G: Check Telstra Outages via TasWater business systems | N/A | Delay built in at SCADA, Attend site and pump down the well, if required. Check the modem is powered (indicator lights)
Note on A48: Sean Gardam: Summaryalarm from RTU internal fault registers

## Matrix
Alarm Severity |  | Consequence Rating
|  | Insignificant | Minor | Moderate | Major | Catastrophic
Time to Rectify | Immediate | High | High | Critical | Critical | Critical
| 24 Hours | High | High | High | Critical | Critical
| 1 Week | Low | Low | Low | Design Issue | Design Issue
Table 9 Severity Selection – Rectification Time versus Consequence
from TOMSTD02 -TasWater Alarm Philosophy for SCADA ALARMS

## Lists
Consequence Type | Consequence Rating | Time To Rectify | Criticality | Delay | Escalation | Alarm Assignment | Setpoint Authority | Latching | Alarm Reset
Financial | Insignificant | Immediate | Critical | N/A | None | Alarm | Operator | Latched | Auto Reset
HSE | Minor | 24 Hours | High | 60 secs | High | Event | Supervisor | Not Latched | SCADA Device Reset
Quality | Moderate | 1 Week | Low | 10 mins | Critical | Design Issue | Manager |  | SCADA General Reset
Property | Major |  | Maint | 15 mins |  | Delete | SCADA Engineer |  | Field Reset
Service | Catastrophic |  | Event | 30 mins |  |  | Other |  | Keyswitch
Reputation |  |  | Delete | 60 mins |  |  | N/A
Environment |  |  |  | 4 Hours
Compliance |  |  |  | 12 Hours
24 Hours